The impact of hospital ward ventilation on airborne pathogen exposure

Nicola Mingotti1*, Dorothy Grogono2,3,5*, Gennaro dello Ioio1*, Martin Curran4, Kathryn Barbour2, Marlene Taveira2, Josie Rudman2, Charles S. Haworth2,3, R. Andres Floto2,3,5, Andrew W. Woods1,5

*Contributed equally

1. BP Institute for Multiphase Flow, University of Cambridge, Cambridge, UK

2. Cambridge Centre for Lung Infection, Royal Papworth Hospital, Cambridge, UK

3. Molecular Immunity Unit, University of Cambridge Department of Medicine, MRC Laboratory of Molecular Biology, Cambridge, UK

4. Public Health Laboratory, Cambridge University Hospitals, Cambridge, UK

5. Cambridge Infectious Diseases Interdisciplinary Research Centre, Cambridge, UK

Correspondence to:

Andrew W. Woods

BP Institute for Multiphase Flow, University of Cambridge, Cambridge, CB3 0EZ, UK

aww1@cam.ac.uk

Charles S. Haworth

Royal Papworth Hospital, Cambridge, CB2 0AY, UK

charles.haworth@nhs.net

R. Andres Floto

MRC Laboratory of Molecular Biology, University of Cambridge, Cambridge, CB2 0QH, UK

arf27@cam.ac.uk

All authors contributed to the manuscript according to the four ICMJE criteria for authorship.

Author degree credentials: Nicola Mingotti Ph.D.1*, Dorothy Grogono B.Sc., M.B.,Ch.B., Ph.D.2,3,5*, Gennaro dello Ioio Ph.D.1*, Martin Curran Ph.D.4, Kathryn Barbour R.N.2, Marlene Taveira R.N.2, Josie Rudman RGN RNT MSC PGcertME B.Sc.2, Charles S Haworth M.B.,Ch.B., M.D.2,3, R. Andres Floto B.M., B.Ch.,Ph.D.2,3,5, Andrew W. Woods B.A., M.A., Ph.D.1,5

Acknowledgements:

We are grateful to William G Lindsley (US CDC) for providing the NIOSH air samplers, and Colin Glen for providing information about hospital floor plans and ventilation systems. This work was funded by the Wellcome Trust, Cambridge NIHR Biomedical Research Centre, and Royal Papworth Hospital.

Short running head: Hospital ventilation and airborne pathogen exposure

The COVID-19 pandemic has brought into sharp focus the importance of protecting patients and healthcare workers (HCW) from nosocomial infection1. Hospital-associated infection can occur through contact with contaminated surfaces, by droplets generated by coughing or sneezing settling on exposed mucous membranes, or through direct inhalation of aerosols. Whilst the contribution of each route differs according to the setting and type of infection, the ventilation within hospitals are a key determinant of infection risk from airborne pathogens2,3, with low ventilation rates associated with increased risks of transmission of, for example, tuberculosis and Middle East respiratory syndrome (MERS) 4,5. For patients with cystic fibrosis (CF), acquisition of multidrug-resistant pathogens from other patients represents one of the greatest threats to health6, with both experimental data7 and room sampling8 highlighting the risk of cross infection through long-lived infectious aerosols.

As a direct response to these challenges, Royal Papworth Hospital installed a bespoke ventilation system during its relocation from a 100-year-old facility to a new state-of-the-art cardiothoracic hospital in Cambridge, UK. While the old CF centre relied on passive, natural ventilation, with airflow created by opening doors and windows, mechanical ventilation in the new hospital provides 15 air changes per hour (ACH) in the CF Centre (both patient rooms and corridors), and 6 ACH in other clinical areas.

We examined the impact of high frequency air changes within patient rooms by monitoring the dispersal, mixing, and ventilation of an injected tracer gas (CO2) using eight GSS-CozIR-A sensors in the new and old hospitals, just before occupation and just after vacation respectively, while the heating and ventilation systems were operational. While CO2 persisted in passively ventilated rooms for over 58 minutes, rooms actively ventilated at 6 or 15 ACH experienced exponential decay of tracer concentrations to 10% within 26.7 and 11.7 minutes respectively (Figure 1A).

The type of ventilation determines the fraction of airborne droplets that settle in the patient’s room before being removed. Since the fall speeds of droplets varies with particle size, the impact of changes in ventilation between old and new hospitals is particularly marked for particles in the respirable size range produced by coughing9 (1–10m in diameter; Figure 1B), indicating that high frequency air changes may reduce transmission risks from aerosols.

We next explored air mixing and dispersal along hospital ward corridors, again using a CO2 tracer with sensors deployed 1.7 to 14.7 m from the CO2 source (Figure 1C). With passive ventilation at the Old Papworth site, CO2 spread rapidly along the corridor and persisted for 30 minutes. At the new site active ventilation (at 6 ACH) limited dispersal distances and improved clearance rates (although detectible levels of CO2 remained after 30 minutes) while high 15 ACH ventilation, initially caused faster dispersal than conventional ventilation but led to clearance of CO2 to below 10% of peak levels by 13.3 minutes.

To examine the impact of ventilation on patient exposure to airborne pathogens, we deployed static NIOSH BC 251 two-stage cyclone aerosol samplers9, positioned at 90 and 180 cm from the floor, to sample air in unoccupied patient rooms and in ward corridors in both old and new CF centres during periods of similar ward bed occupancy (92  3.5% new vs 94  7.9% old ward; mean  sd, p = 0.43). The amounts of total bacteria (quantified by 16S qPCR) were reduced in rooms and corridors with high frequency air changes compared to those with passive ventilation (Figure 1D), suggesting reduced patient and HCW exposure to nosocomial airborne infections.

We also considered how people walking might influence air mixing and residence times in corridors. Given the high Reynolds number associated with a person walking (Re = uL/ ~ 0.5 x 105; based on a speed (u) of 1m/s, size (L) of 0.5m, air viscosity () ofPa s, and density ()of1 kg/m3), we expect the resultant wake to drive highly turbulent mixing. When measured in hospital corridors, a person walking along the corridor every 30 seconds considerably increased the residence time of CO2 following a pulse release (Figure 1E), lengthening the half-life from 1.3 minutes to 6.7 minutes (Figure 1E).

Finally, we explored the potential for movement of infectious aerosols between corridors and rooms. We found that CO2 released in the corridor rapidly penetrated into patient rooms with open doors (Figure 1F), despite the fact that both corridor and rooms had their own balanced system of inflow and outflow ducts and were at the same pressure. We saw a steep relationship between the duration of door opening and the resulting CO2 concentrations in the room (Figure 1G), suggesting that limiting door opening could greatly reduce corridor-to-room pathogen spread.

We also noticed that movement of CO2 into rooms increases with temperature contrasts. Air flow speeds across a doorway based on video recordings of tracer smoke show air flowed out of the room near the top (with mean speeds of 15-16 cm/s); while at lower heights air flowed into the room (at 16-18 cm/s; p = 0.002; Figure 1H). The associated exchange flow driven by a 3 oC temperature difference between room and corridor (0.16 m3/s) is comparable in magnitude to the high frequency ventilation (about 0.20 m3/s), and may contribute to pathogen transmission between room and corridor.

In summary, our results indicate that high frequency ventilation can reduce residence times of infectious aerosols, despite residual impacts of people walking in corridors and temperature-dependent exchange flow across doorways. We believe that this strategy has the potential to improve safety for CF patients and other vulnerable individuals in hospital, and impede cross-infection between HCW and patients. Airborne transmission has been implicated in the spread of several nosocomial infections3,6, most recently SARS-CoV21, which remains viable in aerosols for over 3 hours10, and is likely to be transmitted by both large and small airborne droplets3. Enhanced hospital ventilation, coupled with limiting door opening times, equilibration of temperature, minimising corridor traffic, and wearing facemasks, could play a critical role in the response to this current pandemic.

References

1.Guo ZD, Wang ZY, Zhang SF, Li X, Li L, Li C, Cui Y, Fu RB, Dong YZ, Chi XY, Zhang MY, Liu K, Cao C, Liu B, Zhang K, Gao YW, Lu B, Chen W. Aerosol and surface distribution of Severe Acute Respiratory Syndrome Coronavirus 2 in hospital wards, Wuhan, China, 2020. Emerg Infect Dis 2020 Jul;26(7):1583-1591.

2. World Health Organisation Guideline: Natural ventilation for infection control in health-care settings. 2009.

3. Morawska L, Tang JW, Bahnfleth W, Bluyssen PM, Boerstra A, Buonanno G, Cao J, Dancer S, Floto A, Franchimon F, Haworth C, Hogeling J, Isaxon C, Jimenez JL, Kurnitski J, Li Y, Loomans M, Marks G, Marr LC, Mazzarella L, Melikov AK, Miller S, Milton DK, Nazaroff W, Nielsen PV, Noakes C, Peccia J, Querol X, Sekhar C, Seppänen O, Tanabe SI, Tellier R, Tham KW, Wargocki P, Wierzbicka A, Yao M. How can airborne transmission of COVID-19 indoors be minimised? Environment International (2020) doi: https://doi.org/10.1016/j.envint.2020.105832.

4. Fennelly KP, Nardell EA. The relative efficacy of respirators and room ventilation in preventing occupational tuberculosis. Infection Control and Hospital Epidemiology, 1998, 19(10):754–759.

5. Jo S, Hong J, Lee S-E, Ki M, Choi BY, Sung M. Airflow analysis of Pyeongtaek St Mary's Hospital during hospitalization of the first Middle East respiratory syndrome patient in Korea. R Soc Open Sci 2019; 6(3): 181164.

6. Saiman L, Siegel JD, LiPuma JJ, Brown RF, Bryson EA, Chambers MJ, Downer VS, Fliege J, Hazle LA, Jain M, Marshall BC, O'Malley C, Pattee SR, Potter-Bynoe G, Reid S, Robinson KA, Sabadosa KA, Schmidt HJ, Tullis E, Webber J, Weber DJ; Cystic Fibrous Foundation; Society for Healthcare Epidemiology of America. Cystic Fibrosis Foundation infection prevention and control guideline for cystic fibrosis: 2013 update. Infect Control and Hosp Epidemiol 2014;35(S1):S1-S67.

7. Wainwright CE, France MW, O’Rourke P, Anuj S, Kidd TJ, Nissen MD, Sloots TP, Coulter C, Ristovski Z, Hargreaves M, Rose BR, Harbour C, Bell SC, Fennelly KP. Cough-generated aerosols of Pseudomonas aeruginosa and other Gram-negative bacteria from patients with cystic fibrosis. Thorax 2009;64:926–931.

8. Wood ME, Stockwell RE, Johnson GR, Ramsay KA, Sherrard LJ, Kidd TJ, Cheney J, Ballard EL, O'Rourke P, Jabbour N, Wainwright CE, Knibbs LD, Sly PD, Morawska L, Bell SC. Cystic fibrosis pathogens survive for extended periods within cough-generated droplet nuclei. Thorax 2019 Jan;74(1):87-90.

9. Blachere F, Lindsley WG, Pearce TA, Anderson SE, Fisher M, Khakoo R, Meade BJ, Lander O, Davis S, Thewlis RE, Celik I, Chen BT, Beezhold DH.  Measurement of airborne influenza virus in a hospital emergency department. Clin Infect Dis. 2009;48(4):438-440.

10. van Doremalen N, Bushmaker T, Morris DH, Holbrook MG, Gamble A, Williamson BN, Tamin A, Harcourt JL, Thornburg NJ, Gerber SI, Lloyd-Smith JO, de Wit E, Munster VJ. Aerosol and Surface Stability of SARS-CoV-2 as Compared with SARS-CoV-1. N Engl J Med. 2020; 382(16):1564-1567.

Figure Legends

Figure 1. The impact of ventilation on air handling in hospitals

A. Concentrations of tracer gas (CO2) monitored over time following pulse release in a three patient rooms with 15 air changes per hour (ACH; black line) within New Papworth CF Centre, 6 ACH (red line) within New Papworth Hospital, or passive ventilation (blue line) from Old Papworth Hospital. Concentrations normalised to maximum recorded value. B. Model prediction of the fraction of airborne droplets which sediment to the floor or are ventilated in a patient room as a function of mean droplet diameter, shown for rooms passively ventilated (blue), or with 6 (red) or 15 (black) ACH. C. Variations in CO2 concentration after tracer release (at the point marked by star) measured by sensors located along ward corridors (as shown in floor plans) in Old Papworth Hospital under passive ventilation (left), New Papworth Hospital in areas with 6 ACH ventilation (middle) or 15 ACH ventilation (right). Upper panels show normalised CO2 concentrations detected over time by each sensor. Lower panels shown normalised CO2 concentrations as a distance-time plot. D. Comparison of the relative amounts of total bacteria (16S) (quantified by qPCR) detected in air samples from ward corridors and unoccupied rooms in old Papworth Hospital (blue), under passive ventilation, compared to equivalent areas in new Papworth Hospital receiving 15 ACH ventilation (red) during periods of similar ward bed occupancy levels. E. CO2 concentrations over time following tracer release in a corridor with 15 ACH ventilation, in the presence (red) or absence (black) of people walking along it. F. CO2 concentrations over time following tracer released in corridor (red star) measured by sensors deployed along corridor and in-patient rooms. G. Peak CO2 concentrations detected in rooms (expressed as a fraction of maximum corridor concentration) as a function of the time the doorway is kept open. H. Variation of the airflow speed across a doorway as a function of height above the floor (quantified from video of smoke released from an Artic Hayes pen), when the room is 0.5 oC (red) or 1.5 oC (black) hotter than the corridor.